## Summary
SUMMARY
Sr. No | Description | Amount | Total Amount
1 | For School 1 (Installation)
| Filtration Plant | 0
| Fiber Glass Room + Fittings | 0
0
Signage: 4'*2' 24 gauge SS Silver Colored
Message: 4'*2' 24 gauge SS Silver Colored
Ground breaking expense
Inauguration expense
2 | For School 2 (Installation)
| Filtration Plant | 0
| Fiber Glass Room + Fittings | 0
0
Signage: 4'*2' 24 gauge SS Silver Colored
Message: 4'*2' 24 gauge SS Silver Colored
Ground breaking expense
Inauguration expense
3 | For School 3 (Connection) |  | 0
Signage: 4'*2' 24 gauge SS Silver Colored
Message: 4'*2' 24 gauge SS Silver Colored
4 | For School 4 (Connection) |  | 0
Signage: 4'*2' 24 gauge SS Silver Colored
Message: 4'*2' 24 gauge SS Silver Colored
Sub-Total |  |  | 0
ADD
| Contingency 5% |  | 0
| Tax 9.5% |  | 0
Total |  |  | 0
This amount is inclusive of all taxes

## Filtration Plant BOQ
Provision / Install Water Filtration Plant
P/Installation, Testing and Commissioning of Filtration Plant capacity of 500 Liters per hour approved with all accessories and water supply system complete in all respect, to the entire satisfaction of Engineer In charge.
Activity | Water Filtration Plant | P/Installation, Testing and Commissioning of Filtration Plant capacity of 2000 Liters per hour filtration System, Complete in all Respect, Contractor will ensure & Provide Post Installation Water Quality Test from Pakistan Council of Research in Water Resources (PCRWR) , |  | 1 | Nos |  |  |  | 0
Contractor is duly responsible to Ensure Water Quality as safe & hygiene drinking water. Plant is subjected to the approval of concerned Engineer at site.
Total Amount | [8 empty] | 0
Sr. No | Description |  | Specifications |  |  | Make/Size | Qty. | Rate | Amount
1 | Low pressure feed pump CNP new |  | Make: Felsom or CNP/ Italy(Ref) | Material: SS304/SS316 | Model: 70 psi Max. 2hp | 1 hp | 1
|  |  | Capacity: 12 m3/h | Discharge Pressure: 4 bar | Type: Centrifugal
2 | Vessel for Multimedia Filter |  | Size: 13"*54" | Backwash: 3-way valve manual 1" | Media: Hi-Silica Gravel Sand | 13"*54" | 1
3 | Vessel for activated carbon filter |  | Size: 13"*54" | Backwash: 3-way valve manual 1" | Media: Granula Activated Carbon | 13"*54" | 1
4 | Multiple 3 Way Valve 1" (Manual) One for each vessel |  |  |  |  | 1" | 2
5 | Housing + Catridge PPF |  | Size: 20" | PPF Jumbo | 5 micron | J-20"-5 | 1
6 | Housing + Catridge PPY |  | Size: 20" | PPY Jumbo | 1 micron | J-20"-1 | 1
7 | Pressure Guages + Switches |  | Stainless Steel low and high pressure guages | 2.5" dia | Material: SS316 | 2.5" | 2
8 | Online TDS meter |  | Make: Create / Kamatsu | Location: Permeate Line | Range: 0-1000 us/cm or 0-2000 us/cm | China or best quality possible | 1
9 | Control panel |  | Indoor Installation with front access | Material: MS | Local made | Best Quality Possible | 1
10 | UV Lamps + Panels |  | Lamp: Philips (Poland) or Atlantic | Quartz: Aqua Guard | Chamber: Local (Double) Panel: MS powder coated | 33" Philips or Atlantic made | 2
11 | Fitting UPVC |  | Material: UPVC | Era, Taiwan | Size: 1" | Era | 1
12 | Sand Media |  | Model of Vessel: 16" * 65" | Material: Fiber Reinforced Plastic | Design Pressure: 150 Psi | Best Quality Possible | 200KG
|  |  | Make of Vessel: Pentair | Operation: Manual | Type of Control Valve: Side Mounted
|  |  | Make of Valve: Imported | Filling media: China Sand | Piping: UPVC
13 | Carbon |  | Model of Vessel: 16" * 65" | Material: Fiber Reinforced Plastic | Design Pressure: 150 Psi | Holland | 25KG
|  |  | Make of Vessel: Pentair | Operation: Manual | Type of Control Valve: Side Mounted
|  |  | Make of Valve: Imported | Filling Media: Activated Carbon | Piping: UPVC
14 | Jumbo Housing |  |  |  |  | Taiwan | 2
15 | 500 Gallon Storage Tank with float switches; S/F LDPE tanks, 5 layers, white, capacity 500 Gallons with complete accessories and fittings |  |  |  |  | Local | 1
16 | P/F MS pipe Skid Frame overall size of the frame 4' x 10' ; dimensions 1.5" x 1.5" for main frame and 1" x 1" for supports; thickness SWG 12 Gauge; moveable - wheels attached |  |  |  |  | Mild steel | 1

## Fiber Glass Room + Fittings
Providing and Fixing Fiber Glass Room
Sr. No | Description | Qty | L | W | H |  |  | Amount
1 | P/F MS frame for fiber glass installation - frame gauge SWG 18 - 1.5" square pipe for main structure (coulumns/staff); - frame gauge SWG 18 - 1" square pipe for supports; painted fixing and fittings complete in all respects including bolting or concreting as per the site situation
|  | 2 | 10 |  | 10 | 200 | Sft
|  | 2 | 12 |  | 10 | 240 | Sft
|  | 1 | 16 | 14 |  | 224 | Sft
[5 empty] | Total | 664 | Sft
[5 empty] | @ |  | Per Sft
2 | P/F 3 Ply (1.5 mm) fiber reinforce plastic of good quality double sided; for outer side PEPSICO blue color; for inner side PEPSICO white color; complete in all respects
|  | 4 | 10 |  | 10 | 400 | Sft
|  | 4 | 12 |  | 10 | 480 | Sft
|  | 2 | 16 | 14 |  | 448 | Sft
[5 empty] | Total | 1328 | Sft
[5 empty] | @ |  | Per Sft
3 | S/F HDPE pipe PN-16, PE-100, dia 25 mm with complete fittings and fixing
|  | 1 | 100 |  |  | 100 | Rft
[5 empty] | Total | 100 | Rft
[5 empty] | @ |  | Per Rft
4 | S/F PPRC pipe with fittings PN-20, diameter 32 mm, complete services
|  | 1 | 20 |  |  | 20 | Rft
[5 empty] | Total | 20 | Rft
[5 empty] | @ |  | Per Rft
5 | S/F LDPE tanks, 5 layers, white, capacity 500 Gallons with complete accessories and fittings
|  | 2 |  |  |  | 2 | No.
[5 empty] | @ |  | Each
6 | Providing and Fixing of Bib Cocks of steel made ,good Quality, Best for Commercial use, ( Master or equivalent)
|  | 4 |  |  |  | 4 | No.
[5 empty] | @ |  | Each
Total | [7 empty] | 0

## School Connections
School Connections
1 | S/F HDPE pipe PN-16, PE-100, dia 25 mm with complete fittings and fixing
|  | 1 |  | 100 | Rft
|  |  | @ |  | Per Rft
2 | S/F PPRC pipe with fittings PN-20, diameter 32 mm, complete services
|  | 1 |  | 20 | Rft
|  |  | @ |  | Per Rft
3 | S/F LDPE tanks, 5 layers, white, capacity 500 Gallons with complete accessories and fittings
|  | 2 |  | 2 | No.
|  |  | @ |  | Each
4 | Providing and Fixing of Bib Cocks of steel made ,good Quality, Best for Commercial use, ( Master or equivalent)
|  | 4 |  | 4 | No.
|  |  | @ |  | Each
Total | [5 empty] | 0